## Slide 1
An Improved AI-Driven LVAC Network Fault Detection and Classification
Motivation
The increasing integration of low-carbon technologies (LCTs), including PV, EVs and BESS, is reshaping LVAC fault behaviour through bidirectional power flows, inverter-limited fault currents, phase imbalance and control-driven transients. These effects challenge conventional fixed-threshold overcurrent protection.
Although fault detection and classification (FDC) has been widely investigated in transmission-level, medium-voltage and DC networks, dedicated studies for LCT-integrated LVAC feeders remain limited, particularly under practical monitoring constraints, noisy measurements and high-impedance fault conditions.
This study aims to enhance LVAC fault detection and classification using a robust CNN-LSTM-Transformer framework based on limited and measurements.
Method/Approach
Recent FDC approaches are summarised to clarify the methodological gap and motivate the proposed hybrid architecture.
Objects of investigation
A UK suburban LVAC distribution network is modelled in MATLAB/Simulink using core network data provided by SP Energy Networks (SPEN). The system is supplied by a 20 kV/400 V transformer and configured as a 400/230 V, 50 Hz, three-phase four-wire network with a solidly grounded neutral.
The feeder includes mixed three-phase and single-phase loads, together with a 25 kW PV-BESS unit connected via a power-electronic interface, representing phase imbalance, inverter-interfaced dynamics and altered fault-current behaviour.
A single feeder-head measurement point records and as the sole input for FDC, reflecting practical LV monitoring constraints.
Test scenarios cover LG, LL, LLG and LLL faults across Nodes 1–8, downstream HIFs with 50 Ω and 100 Ω resistance, and noise-contaminated measurements for robustness assessment.
Study Committee B5
PROTECTION AND AUTOMATION
Paper ID: 12071
James YU1 | Francisco FILGUEIRA2 | Mikaelle DINIZ3 | Yue QI4 | Jiwei LI4 | Miaorui MA4 | Jin YANG4
1CIGRE UK | 2CIGRE SPAIN | 3Scottish Power Energy Networks UK | 4University of Glasgow UK |  |  | 
yugem@ hotmail.com | patxi.pazos@ yahoo.com | mlopes@ spenergynetworks.co.uk | yue.qi@ gla.ac.uk | jiwei.li.2@ gla.ac.uk | miaorui.ma@ gla.ac.uk | jin.yang@ gla.ac.uk
Figure 1. Topology of the studied UK LVAC network
Category | Representative Methods | Key limitations
Model- and signal-based methods | Observers; Time/frequency analysis | Parameter, feature and noise sensitivity
Knowledge- based | SVM, DT, ANN | Manual features; weak temporal modelling
Deep learning- based | CNNs, LSTMs, Transformers | Higher complexity; data dependence
Table 1. Overview of recent methods in power system FDC
To address these limitations, this study develops an end-to-end CNN-LSTM-Transformer framework for LVAC fault detection and classification.
The measured and signals are segmented into fixed-length post-fault time windows and normalised to reduce operating-condition variation and measurement noise. The resulting six-channel time-series data are used directly as model inputs, without manually engineered protection features.
The CNN front-end enhances inter-phase voltage-current features, the LSTM module captures short-term fault transients, and the Transformer encoder models long-range dependencies associated with inverter-dominated LVAC fault dynamics.
Task-specific output layers perform fault recognition and fault type classification. Model performance is evaluated using accuracy, precision, recall, F1-score and detection latency under load-only, LCT-integrated, noisy and HIF conditions.
Figure 2. The proposed CNN-LSTM-Transformer model for LVAC FDC

## Slide 2
An Improved AI-Driven LVAC Network Fault Detection and Classification
Experimental setup & test results
Four controlled case studies are designed to evaluate the accuracy, robustness and response performance of the proposed CNN-LSTM-Transformer FDC framework under practical LVAC operating conditions.
Discussion
LCT integration slightly reduces classification performance and increases detection latency from 0.14 ms to 0.71 ms, which is expected due to inverter-driven transients and reduced fault-current visibility.
The stable performance under noisy measurements indicates that the proposed framework extracts robust spatio-temporal fault features rather than relying only on current magnitude or manually engineered indicators.
HIF subclass confusion is expected because different impedance levels produce similar weak fault signatures; however, the merged HIF recognition accuracy of approximately 99% is more relevant for practical LV protection.
Conclusion
A CNN-LSTM-Transformer FDC framework is developed for LCT-integrated LVAC networks under limited monitoring conditions.
The framework shows near-perfect FDC performance under load-only operation, with approximately 100% faulted-sample detection and 99.4% normal-state identification, while maintaining classification metrics above 99.5% under LCT integration.
Results under noisy measurements and HIF conditions demonstrate strong robustness, supporting data-driven protection for future LVAC networks.
Study Committee B5
PROTECTION AND AUTOMATION
Paper ID: 12071
Case | Test condition | Key purpose
1 | Load-only LVAC | Baseline FDC performance
2 | LCT-integrated | Impact of inverter-interfaced dynamics
3 | Noisy LCT- integrated | Robustness to measurement uncertainty
4 | HIF, 50 Ω / 100 Ω | Recognition of weak fault signatures
Table 2. Experimental case studies for LVAC FDC
Under conventional load-only operation, the model achieves 100.0% fault detection accuracy and fault classification accuracies above 99.7%, with an average detection latency of 0.14 ms.
With LCT integration, reliable FDC performance is maintained despite inverter-driven waveform distortion. Classification metrics remain above 99.5%, and the average detection latency increases modestly to 0.71 ms.
Under noisy measurements, only marginal variations are observed in accuracy, precision, recall and F1-score, confirming strong robustness against sensing uncertainty.
For HIF conditions, subclass confusion occurs between 50 Ω and 100 Ω faults due to similar electrical characteristics. When merged into a single HIF category, the overall HIF recognition accuracy reaches approximately 99%.
Figure 3. Baseline FDC performance under load-only operation.
Figure 4. FDC performance under LCT-integrated operation.
Figure 5. Noise robustness under LCT-integrated operation.
Figure 6. HIF classification performance.